## natural gas
NOTES: | Commercial boilers: |  | < 10x106btu/hr |  |  | PM10 = PM , includes filterable and condensable
| Industrial boilers: |  | 10 - 100x106btu/hr |  |  | LNB = low NOX burners
| Utility boilers: |  | > 100x106btu/hr |  |  | FGR = flue gas recirculation
| Factors may require changing for specific circumstances |  |  |  |  | This spreadsheet helps estimate a facility's potential to emit. It is provided for the convenience of the permitted community. DHEC does not guarantee the accuracy or appropriateness of this information. Emission factor sources are subject to revision or correction. It is the permittee's responsibility to verify the accuracy of the information. DHEC is not liable for errors or omissions.
Natural Gas - Small (<100) Uncontrolled
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/SCF: | 1020
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/106 SCF- | 7.6 | 7.6 | 7.6 | 0.6 | 100 | 84 | 5.5 | 120000 | 0.0005
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 Fifth Edition, Tables 1.4-1,-2, 7/98 Update
Natural Gas - Small (<100) Uncontrolled LNB
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/SCF: | 1020
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/106 SCF- | 7.6 | 7.6 | 7.6 | 0.6 | 50 | 84 | 5.5 | 120000 | 0.0005
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 Fifth Edition, Tables 1.4-1,-2, 7/98 Update
Natural Gas - Small (<100) Controlled LNB / FGR
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/SCF: | 1020
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/106 SCF- | 7.6 | 7.6 | 7.6 | 0.6 | 32 | 84 | 5.5 | 120000 | 0.0005
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 Fifth Edition, Tables 1.4-1,-2, 7/98 Update
Natural Gas - Large (>100) Wall Fired Pre NSPS Uncontrolled
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/SCF: | 1020
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/106 SCF- | 7.6 | 7.6 | 7.6 | 0.6 | 280 | 84 | 5.5 | 120000 | 0.0005
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 Fifth Edition, Tables 1.4-1,-2, 7/98 Update
Natural Gas - Large (>100) Wall Fired Post-NSPS Uncontrolled
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/SCF: | 1020
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/106 SCF- | 7.6 | 7.6 | 7.6 | 0.6 | 190 | 84 | 5.5 | 120000 | 0.0005
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 Fifth Edition, Tables 1.4-1,-2, 7/98 Update
Natural Gas - Large (>100) Wall Fired Controlled LNB
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/SCF: | 1020
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/106 SCF- | 7.6 | 7.6 | 7.6 | 0.6 | 140 | 84 | 5.5 | 120000 | 0.0005
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 Fifth Edition, Tables 1.4-1,-2, 7/98 Update
Natural Gas - Large (>100) Wall Fired Controlled FGR
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/SCF: | 1020
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/106 SCF- | 7.6 | 7.6 | 7.6 | 0.6 | 100 | 84 | 5.5 | 120000 | 0.0005
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 Fifth Edition, Tables 1.4-1,-2, 7/98 Update
Natural Gas - Tangential Fired Uncontrolled
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/SCF: | 1020
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/106 SCF- | 7.6 | 7.6 | 7.6 | 0.6 | 170 | 24 | 5.5 | 120000 | 0.0005
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 Fifth Edition, Tables 1.4-1,-2, 7/98 Update
Natural Gas - Tangential Fired Controlled FGR
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/SCF: | 1020
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/106 SCF- | 7.6 | 7.6 | 7.6 | 0.6 | 76 | 98 | 5.5 | 120000 | 0.0005
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 Fifth Edition, Tables 1.4-1,-2, 7/98 Update

## fuel oil
NOTES: | Commercial boilers: |  | < 10x106btu/hr |  |  | LNB = low NOX burners |  |  | This spreadsheet helps estimate a facility's potential to emit. It is provided for the convenience of the permitted community. DHEC does not guarantee the accuracy or appropriateness of this information. Emission factor sources are subject to revision or correction. It is the permittee's responsibility to verify the accuracy of the information. DHEC is not liable for errors or omissions.
| Industrial boilers: |  | 10 - 100x106btu/hr |  |  | FGR = flue gas recirculation
| Utility boilers: |  | > 100x106btu/hr
PM, PM10, and PM2.5 include condensible component
* Footnote (a) of Table 1.3-11, "Emissions Factors for Metals from Uncontrolled No. 6 Fuel Oil Combustion", indicates that this is data for all residual oil boilers, not just No. 6 fuel oil.
Factors may require changing for specific circumstances
Distillate (#2) Oil Fired (< 10 mmbtu/hr)
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/gal: | 140000 |  | % Sulfur: | 0.05
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb**
lb/103 gal- | 3.3 | 2.38 | 2.13 | 7.1 | 20 | 5 | 0.34 | 22300 | 9
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 5th Ed, Tables 1.3-1,-2,-3,-7 5/2010 Update
**Pb is in units of (lb/1012 BTU)
Distillate (#2) Oil Fired (10 - 100 mmbtu/hr)
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/gal: | 140000 |  | % Sulfur: | 0.05
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb**
lb/103 gal- | 3.3 | 2.3 | 1.55 | 7.1 | 20 | 5 | 0.2 | 22300 | 9
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 5th Ed, Tables 1.3-1,-2,-3,-6 5/2010 Update
**Pb is in units of (lb/1012 BTU)
Distillate (#2) Oil Fired (> 100 mmbtu/hr)
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/gal: | 140000 |  | % Sulfur: | 0.05
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb**
lb/103 gal- | 3.3 | 2.3 | 1.55 | 7.1 | 24 | 5 | nd | 22300 | 9
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | nd | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | nd | No Input | No Input
Source: AP-42 5th Ed, Tables 1.3-1,-2,-3,-6 5/2010 Update
**Pb is in units of (lb/1012 BTU)
Distillate (#2) Oil Fired (> 100 mmbtu/hr) LNB / FGR
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/gal: | 140000 |  | % Sulfur: | 0.05
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb**
lb/103 gal- | 3.3 | 2.3 | 1.55 | 7.1 | 10 | 5 | nd | 22300 | 9
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | nd | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | nd | No Input | No Input
Source: AP-42 5th Ed, Tables 1.3-1,-2,-3,-6 5/2010 Update
**Pb is in units of (lb/1012 BTU)
#4 Oil Fired (< 10 mmbtu/hr)
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/gal: | 145000 |  | % Sulfur: | 1.5
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/103 gal- | 8.5 | 5.8428 | 3.1128 | 225 | 20 | 5 | 0.34 | 25000 | 0.00151
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 5th Ed, Tables 1.3-1,-2,-3,-7, -11 5/2010 Update
#4 Oil Fired (10 - 100 mmbtu/hr)
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/gal: | 145000 |  | % Sulfur: | 1.5
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/103 gal- | 8.5 | 7.5228 | 5.4228 | 225 | 20 | 5 | 0.2 | 25000 | 0.00151
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 5th Ed, Tables 1.3-1,-2,-3,-5, -11 5/2010 Update
#4 Oil Fired (> 100 mmbtu/hr) Normal firing
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/gal: | 145000 |  | % Sulfur: | 1.5
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/103 gal- | 8.5 | 6.456 | 5.112 | 225 | 47 | 5 | 0.76 | 25000 | 0.00151
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 5th Ed, Tables 1.3-1,-2,-3,-4,-11 5/2010 Update
#4 Oil Fired (> 100 mmbtu/hr) Tangential firing
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/gal: | 145000 |  | % Sulfur: | 1.5
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/103 gal- | 8.5 | 6.456 | 5.112 | 225 | 32 | 5 | 0.76 | 25000 | 0.00151
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 5th Ed, Tables 1.3-1,-2,-3,-4, -11 5/2010 Update
#5 Oil Fired (< 10 mmbtu/hr)
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/gal: | 150000 |  | % Sulfur: | 2
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/103 gal- | 11.5 | 7.704 | 3.804 | 314 | 55 | 5 | 1.13 | 25000 | 0.00151
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 5th Ed, Tables 1.3-1,-2,-3,-7, -11 5/2010 Update
#5 Oil Fired (10 - 100 mmbtu/hr)
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/gal: | 150000 |  | % Sulfur: | 2
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/103 gal- | 11.5 | 10.104 | 7.104 | 314 | 55 | 5 | 0.28 | 25000 | 0.00151
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 5th Ed, Tables 1.3-1,-2,-3,-5, -11 5/2010 Update
#5 Oil Fired (> 100 mmbtu/hr) Normal firing
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/gal: | 150000 |  | % Sulfur: | 2
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/103 gal- | 11.5 | 8.58 | 6.66 | 314 | 47 | 5 | 0.76 | 25000 | 0.00151
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 5th Ed, Tables 1.3-1,-2,-3,-4, -11 5/2010 Update
#5 Oil Fired (> 100 mmbtu/hr) Tangential firing
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/gal: | 150000 |  | % Sulfur: | 2
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/103 gal- | 11.5 | 8.58 | 6.66 | 314 | 32 | 5 | 0.76 | 25000 | 0.00151
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 5th Ed, Tables 1.3-1,-2,-3,-4, -11 5/2010 Update
#6 Oil Fired (< 10 mmbtu/hr)
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/gal: | 150000 |  | % Sulfur: | 2.5
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/103 gal- | 27.695 | 17.8889 | 7.5864 | 392.5 | 55 | 5 | 1.13 | 25000 | 0.00151
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 5th Ed, Tables 1.3-1,-2,-3,-7, -11 5/2010 Update
#6 Oil Fired (10 - 100 mmbtu/hr)
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/gal: | 150000 |  | % Sulfur: | 2.5
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/103 gal- | 27.695 | 24.2289 | 16.3039 | 392.5 | 55 | 5 | 0.28 | 25000 | 0.00151
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 5th Ed, Tables 1.3-1,-2,-3,-5, -11 5/2010 Update
#6 Oil Fired (> 100 mmbtu/hr) Normal firing
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/gal: | 150000 |  | % Sulfur: | 2.5
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/103 gal- | 27.695 | 20.203 | 15.131 | 392.5 | 47 | 5 | 0.76 | 25000 | 0.00151
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 5th Ed, Tables 1.3-1,-2,-3,-4, -11 5/2010 Update
#6 Oil Fired (> 100 mmbtu/hr) Normal firing / LNB
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/gal: | 150000 |  | % Sulfur: | 2.5
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/103 gal- | 27.695 | 20.203 | 15.131 | 392.5 | 40 | 5 | 0.76 | 25000 | 0.00151
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 5th Ed, Tables 1.3-1,-2,-3,-4, -11 5/2010 Update
#6 Oil Fired (> 100 mmbtu/hr) Tangential firing
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/gal: | 150000 |  | % Sulfur: | 2.5
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/103 gal- | 27.695 | 20.203 | 15.131 | 392.5 | 32 | 5 | 0.76 | 25000 | 0.00151
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 5th Ed, Tables 1.3-1,-2,-3,-4, -11 5/2010 Update
#6 Oil Fired (> 100 mmbtu/hr) Tangential firing / LNB
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | BTU/gal: | 150000 |  | % Sulfur: | 2.5
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/103 gal- | 27.695 | 20.203 | 15.131 | 392.5 | 26 | 5 | 0.76 | 25000 | 0.00151
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2 | Pb
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 5th Ed, Tables 1.3-1,-2,-3,-4, -11 5/2010 Update

## propane & butane
Propane
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | 106 BTU/103 gal: | 91.5 |  | S gr/100 ft3: | 0.01
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2
lb/103 gal- | 0.7 | 0.7 | 0.7 | 0.001 | 13 | 7.5 | 1 | 12500
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 5th Ed, Tables 1.5-1 7/08 Update
Butane
Parameters: | Rating: |  | MMBTU/hr
| Hours/year: | 8760 |  | 106 BTU/103 gal: | 102 |  | S gr/100 ft3: | 0.01
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2
lb/103 gal- | 0.8 | 0.8 | 0.8 | 0.0009 | 15 | 8.4 | 1.1 | 14300
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 5th Ed, Tables 1.5-1 7/08 Update
This spreadsheet helps estimate a facility's potential to emit. It is provided for the convenience of the permitted community. DHEC does not guarantee the accuracy or appropriateness of this information. Emission factor sources are subject to revision or correction. It is the permittee's responsibility to verify the accuracy of the information. DHEC is not liable for errors or omissions.

## engine
NOTES: | NGR = natural gas-fired reciprocating. For NGR, PM, PM10, and PM2.5 include condensible component
nd = not determined
Dual fuel is based on 95% natural gas, 5% diesel fuel
Emissions for gasoline industrial engines (<250 hp), diesel industrial engines (<600 hp), large stationary diesel
engines, and stationary dual fueled engines can be calculated using power output (in hp or kW) or fuel input.
|  | 1 hp = 0.746 kW |  |  | 1 kW = 1.341 hp
** When necessary, use an average brake-specific fuel consumption (BSFC) of 7,000 Btu/hp-hr to convert from
| lb/MMBtu to lb/hp-hr (as outlined in AP-42, Tables 3.3-1 and 3.4-1). | [6 empty] | This spreadsheet helps estimate a facility's potential to emit. It is provided for the convenience of the permitted community. DHEC does not guarantee the accuracy or appropriateness of this information. Emission factor sources are subject to revision or correction. It is the permittee's responsibility to verify the accuracy of the information. DHEC is not liable for errors or omissions.
Factors may require changing for specific circumstances
No lead emission factors have been determined for these sources.
Gasoline Industrial Engine (< 250 HP)
Parameters: | Rating: |  | HP |  | kW |  | MMBTU/hr **
| Hours/year: | 8760
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2
lb/HP-hr- | 0.000721 | 0.000721 | 0.000721 | 0.000591 | 0.011 | 0.00696 | 0.021591 | 1.08
lb/MMBTU- | 0.1 | 0.1 | 0.1 | 0.084 | 1.63 | 0.99 | 3.03 | 154
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 Fifth Edition, Tables 3.3-1, 10/96 Update
Diesel Industrial Engine (< 600 HP)
Parameters: | Rating: |  | HP |  | kW |  | MMBTU/hr **
| Hours/year: | 8760
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2
lb/HP-hr- | 0.0022 | 0.0022 | 0.0022 | 0.00205 | 0.031 | 0.00668 | 0.0025141 | 1.15
lb/MMBTU- | 0.31 | 0.31 | 0.31 | 0.29 | 4.41 | 0.95 | 0.36 | 164
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 Fifth Edition, Tables 3.3-1, 10/96 Update
Large Stationary Diesel Engine Uncontrolled
Parameters: | Rating: |  | HP |  | kW |  | MMBTU/hr **
| Hours/year: | 8760
| % Sulfur: | 1
Emission Factors: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2
lb/HP-hr- | 0.0007 | 0.00057547 | 0.00055839 | 0.00809 | 0.024 | 0.0055 | 0.000705 | 1.16
lb/MMBTU- | 0.1 | 0.082209 | 0.07977 | 1.01 | 3.2 | 0.85 | 0.0819 | 165
Emissions: | PM | PM10 | PM2.5 | SO2 | NOX | CO | VOC | CO2
lb/hr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
ton/yr- | No Input | No Input | No Input | No Input | No Input | No Input | No Input | No Input
Source: AP-42 Fifth Edition, Tables 3.4-1, -2, 10/96 Update

## File History
Date | Page | Pollutant | Previous Value | New Value | Description of Change
2004-08-17 | Propane | NOX | N/A | 0.0735 lb/mmbtu | With the newly created SC Regulation 61-62.5, Standard No. 5.2, an emission factor reflecting use of low NOx burners when firing propane is needed in the spreadsheet. Currently the spreadsheet has only an uncontrolled emission rate. An EPA technical bulletin issued in November, 1999 contains information indicating that low NOx burners reduce the NOx emissions by 50% which is the factor being added to the spreadsheet.
2004-08-17 | Woodwaste | VOC | 0.0174 lb/mmbtu | 0.017 lb/mmbtu | EPA AP-42 emission factors were researched to determine if any factors have been updated. The only change was found to be with combustion of woodwaste and the only factor that has changed is the VOC factor. That change (-0.0004) was small but reflects the EPA 9/03 update replacing the 3/02 update.
2004-08-17 | Waste Oil | N/A | N/A | N/A | The EPA reference documents for the emission factors were previously incorrectly referenced as coming from EPA's AP-42, Tables 1.3-1, -2, and -3. The reference comes from EPA's AP-42, Tables 1.11-1, -2, and -3 and is being corrected.
2009-10-08 | All but Coal | All | - | - | Added Lead & PM2.5 | CDH
2010-05-20 |  | CO2 | N/A | N/A | Added CO2 | DRC
2010-08-10 | All | All | N/A | N/A | Referenced EPA AP-42 emission factors to determine if any factors and/or derivation methods have been updated and changed those applicable factors and/or methods within the table. | JSD
2010-09-03 | All but Coal | All | N/A | N/A | Updated Format | CDH
2010-10-11 | All but Coal and waste oil | GHGs | N/A | N/A | Added separate GHG calculations based on GHG reporting rule 40 CFR 98 | CDH
2012-06-05 | Fuel Oil | GHGs | N/A | N/A | Corrected CH4 and N2O factors for fuel oil
2014-12-03 | All | GHGs | N/A | N/A | Removed greenhouse gas emission calculations. | MJS